AQR2576NJ CO2/temperature/humidity controller for UP plug as per UL standard

with integrated maintenance- and recalibration-free CO2 sensor,

measuring range 0 5000 ppm,

with ventilation control across 3 settable switching steps for CO2 concentration and 3 switching signal objects On/Off, or one positioning signal object 0…100% to control a ventilation actor,

with temperature control as continuous control (PID algorithm) for pure heating operation, heating and cooling operation, and adjustable positioning variable as continuous positioning signal 0…100%, or as pulse-width modulated (PWM) switching signal On/Off,

with ventilation control across 3 settable switching steps for relative humidity, and 3 switching signal objects On/Off, or one positioning signal object 0…100% to control a ventilation actor,

with setpoints for CO2 concentration, room temperature, and relative humidity adjustable via KNX bus,

with analog input to connect temperature sensors with NTC 10k sensing element to measure room, floor, or ceiling temperature,

measuring range 0…+50,0 °C,

with mean value generation as an alternative via the room temperature values measured via plugged-in sensor module and analog input,

with 2 multi-functional binary inputs to control window contacts or buttons for blinds and/or lighting control,

with monitoring of window status and/or 1-button or 2-button control for lighting and/or solar protection,

with monitoring of room sensor and notification in the event of errors,

with commissioning and control parameters that can be set via ETS,

with KNX communication in S-mode and LTE mode,

with 9-pin socket rail to plug in a sensor module,

with 4 screw terminals to connect a temperature sensor and up to 2 window contacts or buttons via single- or multi-wire lines at max. cross-sections of 1 x 2.5 mm2 / 2 x 1.5 mm2

with electronics operation on bus voltage,

with integrated bus coupler with programming button and LED,

with bus connection via bus terminal, bus load < 15 mA,

as flush-mounted device with mounting plate "UL (portrait)“ to mount in a flush-mounted plug as per the UL standard,

degree of protection: IP 20,

dimensions: 64 x 110 x 39 mm (L x W x H),

Manufacturer: Siemens

Ord. no.: S55720-S210

Note: To complete the device as CO2, room temperature, and/or room humidity controller, a design frame "DELTA azio“ and a sensor module AQR2532NNW,  AQR2533NNW,  AQR2535NNW,  AQR2535NNWQ, or a dummy cover AQR2530NNW are required, and must be ordered separately.